## Table 1
Address Dez | Address Hex | Size | Register Name | Data Type | Ratio | Unit | Attribute | Register description | Notes
16388 | 4004 | 1 | MPVMode | Uint16 |  |  | R | Inverter working mode | 0 ：Initialization 1 ：Waiting 2 ：Running 3 ：Offnet mode，used for energy storage 4 ：Grid on-load mode，used for energy storage 5 ：Fault 6 ：Update 7 ：Test 8 ：Self-checking 9 ：Reset
16389 | 4005 | 2 | HfaultMSG | Uint32 |  |  | R | Display board/slave error message
16391 | 4007 | 2 | MfaultMSG | Uint32 |  |  | R | Master controller error message
16393 | 4009 | 2 | MFaultMSG2 | Uint32 |  |  | R | Master controller error message 2
16395 | 400B | 2 | Reserve |  |  |  | R | BMS error message
16397 | 400D | 2 | Reserve |  |  |  | R | Reserve
16399 | 400F | 1 | Error_Count | Uint16 | 0 |  | R | Number of inverter error warning message
16400 | 4010 | 1 | SinkTemp | Int16 | -1 | ℃ | R | Temperature of radiator
16401 | 4011 | 1 | AmbTemp | Int16 | -1 | ℃ | R | Environment temperature
16402 | 4012 | 1 | GFCI | Int16 | 0 | mA | R | Electric leakage to the flood
16403 | 4013 | 1 | ISO1 | UInt16 | 0 | k Ω | R | PV1+_ISO
16404 | 4014 | 1 | ISO2 | UInt16 | 0 | k Ω | R | PV2+_ISO
16405 | 4015 | 1 | ISO3 | UInt16 | 0 | k Ω | R | PV3+_ISO | 0xffff
16406 | 4016 | 1 | ISO4 | UInt16 | 0 | k Ω | R | PV ISO
16407 | 4017 | 2 | [5 empty] | Reserved bit
16409 | 4019 | 1 | ConnTime | Uint16 | 0 | S | R | Countdown for grid connection
16410 | 401A | 1 | ErrorDataSN | Uint16 | 0 |  | R | Serial number of the fault recording area | Serial number of fault in the fault recording area. For each new fault, the serial number is increased by 1. If the serial number reaches the maximum value of 60000 and another fault is added, the serial number becomes 1；
16411 | 401B | 1 | SettingDataSN | Uint16 | 0 |  | R | Serial number of the parameter setting area | If the data in the Settings area has changed +1
16412 | 401C | 6 | Running_Data | Uint16 | 0 |  | R |  | Pass-through information (for extended information addition to the control board)
16418 | 4022 | 1 | SetAppMode | Int16 | 0 |  | R | Inverter sets the application mode | 0=self-using，1=separate time，2=For electricity，3=passivity
16423 | 4027 | 1 | BatStatusDisp | Uint16 | 0 |  | R | Battery working status | normal，Prohibit charging，Prohibyted discharge ，Prohibyted charging and discharge， strength charge，waked
16424 | 4028 | 1 | BatProtocolSet | Int16 | 0 |  | R | Battery protocol | 0：No using battery 1：Zheng Tai485(deleted） 2：plumbic acid 3：SAJ-CAN 4：DYNESS-48V 5：Guo Neng 485(deleted） 6：GH_485 7：GH_CAN 8：Pai Neng CAN 9：WECO 10:UZ_CAN 11:easyLi-CAN 12:DYNESS-51V 13:SAJ_B2 20:dyness (DYNESS-H) Da Qing 21:pylon (SC0500) Pai Neng 22 saj_can
16425 | 4029 | 1 | BatChgSocUpLimit | Int16 | 0 | % | R | Battery set SOC_H | 0-100
16426 | 402A | 1 | BatDisSocDowLimit | Int16 | 0 | % | R | Battery set SOC_L | 0-100
16427 | 402B | 1 | BatDODSet | Int16 | 0 | % | R | Set battery DOD | 0-100
16428 | 402C | 1 | BatResSoc | Int16 | 0 | % | R | Set the reserved SOC value of the battery | 0-100
16432 | 4030 | 1 | MeterModeSet | Int16 | 0 |  | R | Meter mode which was set | 0：forbid 1：A single phase meter 2：A three-phase electric meter
16433 | 4031 | 1 | RGridVolt | Uint16 | -1 | V | R | R phase grid | Three-phase power grid voltage
16434 | 4032 | 1 | RGridCurr | Int16 | -2 | A | R | R phase grid current
16435 | 4033 | 1 | RGridFreq | Uint16 | -2 | Hz | R | R phase grid frequency
16436 | 4034 | 1 | RGridDCI | Int16 | 0 | mA | R | R phase grid DC component
16437 | 4035 | 1 | RGridPowerWatt | Int16 | 0 | W | R | R phase grid active power
16438 | 4036 | 1 | RGridPowerVA | Uint16 | 0 | W | R | R phase grid apparent power
16439 | 4037 | 1 | RGridPowerPF | Int16 | -3 |  | R | R phase grid power factor
16440 | 4038 | 1 | SGridVolt | Uint16 | -1 | V | R | S-phase grid voltage
16441 | 4039 | 1 | SGridCurr | Int16 | -2 | A | R | S-phase grid current
16442 | 403A | 1 | SGridFreq | Uint16 | -2 | Hz | R | S-phase grid frequency
16443 | 403B | 1 | SGridDCI | Int16 | 0 | mA | R | S-phase grid DC component
16444 | 403C | 1 | SGridPowerWatt | Int16 | 0 | W | R | S-phase grid active power
16445 | 403D | 1 | SGridPowerVA | Uint16 | 0 | W | R | Apparent power of S-phase grid
16446 | 403E | 1 | SGridPowerPF | Int16 | -3 |  | R | S-phase grid power factor
16447 | 403F | 1 | TGridVolt | Uint16 | -1 | V | R | T phase grid voltage
16448 | 4040 | 1 | TGridCurr | Int16 | -2 | A | R | T-phase grid current
16449 | 4041 | 1 | TGridFreq | Uint16 | -2 | Hz | R | T-phase grid frequency
16450 | 4042 | 1 | TGridDCI | Int16 | 0 | mA | R | Dc component of T-phase grid
16451 | 4043 | 1 | TGridPowerWatt | Int16 | 0 | W | R | T phase grid active power
16452 | 4044 | 1 | TGridPowerVA | Uint16 | 0 | W | R | Apparent power of T-phase grid
16453 | 4045 | 1 | TGridPowerPF | Int16 | -3 |  | R | T-phase grid power factor
16454 | 4046 | 1 | RInvVolt | Uint16 | -1 | V | R | R phase inverter voltage | Inverter
16455 | 4047 | 1 | RInvCurr | Int16 | -2 | A | R | R phase inverse current
16456 | 4048 | 1 | RInvFreq | Uint16 | -2 | Hz | R | R phase inverter
16457 | 4049 | 1 | RInvPowerWatt | Int16 | 0 | W | R | R phase inverting active power
16458 | 404A | 1 | RInvPowerVA | Uint16 | 0 | VA | R | R phase inverting apparent power
16459 | 404B | 1 | SInvVolt | Uint16 | -1 | V | R | S phase inverter voltage
16460 | 404C | 1 | SInvCurr | Int16 | -2 | A | R | S phase inverter current
16461 | 404D | 1 | SInvFreq | Uint16 | -2 | Hz | R | S phase inverter frequency
16462 | 404E | 1 | SInvPowerWatt | Int16 | 0 | W | R | S-phase inverse active power
16463 | 404F | 1 | SInvPowerVA | Uint16 | 0 | VA | R | S-phase inverting apparent power
16464 | 4050 | 1 | TInvVolt | Uint16 | -1 | V | R | T phase inverting voltage
16465 | 4051 | 1 | TInvCurr | Int16 | -2 | A | R | T phase inverse current
16466 | 4052 | 1 | TInvFreq | Uint16 | -2 | Hz | R | T-phase inverting frequency
16467 | 4053 | 1 | TInvPowerWatt | Int16 | 0 | W | R | T phase inverting active power
16468 | 4054 | 1 | TInvPowerVA | Uint16 | 0 | VA | R | T-phase inverting apparent power
16469 | 4055 | 1 | ROutVolt | Uint16 | -1 | V | R | R phase output voltage | Off-grid output voltage DC component
16470 | 4056 | 1 | ROutCurr | Uint16 | -2 | A | R | R phase output current
16471 | 4057 | 1 | ROutFreq | Uint16 | -2 | Hz | R | R phase output frequency
16472 | 4058 | 1 | ROutDVI | Int16 | 0 | mV | R | R phase output voltage DC component
16473 | 4059 | 1 | ROutPowerWatt | Uint16 | 0 | W | R | The R phase outputs active power
16474 | 405A | 1 | ROutPowerVA | Uint16 | 0 | VA | R | R phase output apparent power
16475 | 405B | 1 | SOutVolt | Uint16 | -1 | V | R | S phase output voltage
16476 | 405C | 1 | SOutCurr | Uint16 | -2 | A | R | S phase output current
16477 | 405D | 1 | SOutFreq | Uint16 | -2 | Hz | R | S phase output frequency
16478 | 405E | 1 | SOutDVI | Int16 | 0 | mV | R | S phase output
16479 | 405F | 1 | SOutPowerWatt | Uint16 | 0 | W | R | S phase output active power
16480 | 4060 | 1 | SOutPowerVA | Uint16 | 0 | VA | R | S-phase output apparent power
16481 | 4061 | 1 | TOutVolt | Uint16 | -1 | V | R | T phase output voltage
16482 | 4062 | 1 | TOutCurr | Uint16 | -2 | A | R | T phase output current
16483 | 4063 | 1 | TOutFreq | Uint16 | -2 | Hz | R | T phase output frequency
16484 | 4064 | 1 | TOutDVI | Int16 | 0 | mV | R | T phase output voltage DC component
16485 | 4065 | 1 | TOutPowerWatt | Uint16 | 0 | W | R | T phase output active power
16486 | 4066 | 1 | TOutPowerVA | Uint16 | 0 | VA | R | T phase output apparent power
16487 | 4067 | 1 | BusVoltMaster | Uint16 | -1 | V | R | Host BUS voltage | Bus
16488 | 4068 | 1 | BusVoltSlave | Uint16 | -1 | V | R | Slave BUS voltage
16489 | 4069 | 1 | BatVolt | Uint16 | -1 | V | R | The battery voltage | Battery on live
16490 | 406A | 1 | BatCurr | Int16 | -2 | A | R | The battery current
16491 | 406B | 1 | BatCurr1 | Int16 | -2 | A | R | Battery controller 1 Current
16492 | 406C | 1 | BatCurr2 | Int16 | -2 | A | R | Battery controller 2 Current
16493 | 406D | 1 | BatPower | Int16 | 0 | W | R | The battery power
16494 | 406E | 1 | BatTempC | Int16 | -1 | ℃ | R | Battery temperature
16495 | 406F | 1 | BatEnergyPercent | Uint16 | -2 | % | R | Battery electri
16496 | 4070 | 1 | Reserve | Uint16 | 0 |  | R | Reserve | PV
16497 | 4071 | 1 | PV1Volt | UInt16 | -1 | V | R | PV1 voltage
16498 | 4072 | 1 | PV1Curr | UInt16 | -2 | A | R | Total current PV1
16499 | 4073 | 1 | PV1Power | UInt16 | 0 | W | R | PV1 power
16500 | 4074 | 1 | PV2Volt | UInt16 | -1 | V | R | PV2 voltage
16501 | 4075 | 1 | PV2Curr | UInt16 | -2 | A | R | Total current PV2
16502 | 4076 | 1 | PV2Power | UInt16 | 0 | W | R | PV2 power
16503 | 4077 | 1 | PV3Volt | UInt16 | -1 | V | R | PV3 voltage
16504 | 4078 | 1 | PV3Curr | UInt16 | -2 | A | R | PV3 total current
16505 | 4079 | 1 | PV3Power | UInt16 | 0 | W | R | PV3 power
16506 | 407A | 1 | PV4Volt | UInt16 | -1 | V | R | PV4 voltage
16507 | 407B | 1 | PV4Curr | UInt16 | -2 | A | R | PV4 total current
16508 | 407C | 1 | PV4Power | UInt16 | 0 | W | R | PV4 power
16525 | 408D | 1 | ROnGridOutVolt | Uint16 | -1 | V | R | R phase grid-connected side voltage | Side net
16526 | 408E | 1 | ROnGridOutCurr | Uint16 | -2 | A | R | Side current of R phase grid-connected
16527 | 408F | 1 | ROnGridOutFreq | Uint16 | -2 | Hz | R | Side frequency of R phase grid-connected
16528 | 4090 | 1 | ROnGridOutPowerWatt | Uint16 | 0 | W | R | Side active power of R phase grid-connected
16529 | 4091 | 1 | SOnGridOutVolt | Uint16 | -2 | A | R | Side voltage of S phase grid-connected
16530 | 4092 | 1 | SOnGridOutPowerWatt | Uint16 | 0 | W | R | Side active power of S phase on the grid-connected
16531 | 4093 | 1 | TOnGridOutVolt | Uint16 | -2 | A | R | T phase grid-connected side voltage
16532 | 4094 | 1 | TOnGridOutPowerWatt | Uint16 | 0 | W | R | T active power on the grid-connected side
16533 | 4095 | 1 | PV_direction | Uint16 | 0 |  | R | PV Direction of energy flow | 1：PV energy flow 0：PV no output
16534 | 4096 | 1 | Battery_direction | int16 | 0 |  | R | Direction of battery energy flow | 1：The battery discharge 0：No battery energy flow -1：The battery charge
16535 | 4097 | 1 | Grid_direction | int16 | 0 |  | R | Direction of grid energy flow | 1：Grid output 0：No grid energy flow -1：Grid input
16536 | 4098 | 1 | OutPut_direction | Uint16 | 0 |  | R | Direction of energy flow from output to load | 1：from output to load 0：no output energy flow
16544 | 40A0 | 1 | SysTotalLoadWatt | Int16 | 0 | W | R | The total system load consumes power
16545 | 40A1 | 1 | CT_GridPowerWatt | int16 | 0 | W | R | CT real power of the grid | Internal CT acquisition
16546 | 40A2 | 1 | CT_GridPowerVA | int16 | 0 | VA | R | CT Apparent power of the grid
16547 | 40A3 | 1 | CT_PVPowerWatt | int16 | 0 | W | R | CT PV real power
16548 | 40A4 | 1 | CT_PVPowerVA | int16 | 0 | VA | R | CT PV Apparent power
16549 | 40A5 | 1 | TotalPVPower | Int16 | 0 | W | R | PV total power
16550 | 40A6 | 1 | TotalBatteryPower | Int16 | 0 | W | R | Battery total power
16551 | 40A7 | 1 | TotalGridPowerWatt | Int16 | 0 | W | R | Grid total real power
16552 | 40A8 | 1 | TotalGridPowerVA | Int16 | 0 | VA | R | Grid total apparent power
16553 | 40A9 | 1 | TotalInvPowerWatt | Int16 | 0 | W | R | Inverter total real power
16554 | 40AA | 1 | TotalInvPowerVA | Int16 | 0 | VA | R | Inverter total apparent power
16555 | 40AB | 1 | BackupTotalLoadPowerWatt | Uint16 | 0 | W | R | Backup total load real power
16556 | 40AC | 1 | BackupTotalLoadPowerVA | Uint16 | 0 | VA | R | Backup total load apparent power
16557 | 40AD | 1 | SysGridPowerWall | Int16 | 0 | W | R | Gird system real power
16560 | 40B0 | 12 | Reserve | Uint16 | 0 |  | R | reserver
16572 | 40BC | 1 | Today_Hour | Uint16 | -1 | H | R | PV Grid-connected day generation time
16573 | 40BD | 2 | Total_Hour | Uint32 | -1 | H | R | PV Total grid-connected generation time
16575 | 40BF | 2 | Today_PV_Energy | Uint32 | -2 | Kw h | R | PV daily output | PV1 power generation
16577 | 40C1 | 2 | Month_PV_Energy | Uint32 | -2 | Kw h | R | PV monthly output
16579 | 40C3 | 2 | Year_PV_Energy | Uint32 | -2 | Kw h | R | PV annual output
16581 | 40C5 | 2 | Total_PV_Energy | Uint32 | -2 | Kw h | R | PV total output
16583 | 40C7 | 2 | Today_BatChgEnergy | Uint32 | -2 | Kw h | R | Daily battery charge | Battery charge
16585 | 40C9 | 2 | Month_BatChgEnergy | Uint32 | -2 | Kw h | R | Monthly battery charge
16587 | 40CB | 2 | Year_BatChgEnergy | Uint32 | -2 | Kw h | R | Annual battery charge
16589 | 40CD | 2 | Total_BatChgEnergy | Uint32 | -2 | Kw h | R | Total battery charge
16591 | 40CF | 2 | Today_BatDisEnergy | Uint32 | -2 | Kw h | R | Daily battery discharge quantity | Battery discharge
16593 | 40D1 | 2 | Month_BatDisEnergy | Uint32 | -2 | kw h | R | Monthly battery discharge quantity
16595 | 40D3 | 2 | Year_BatDisEnergy | Uint32 | -2 | Kw h | R | Annual battery discharge quantity
16597 | 40D5 | 2 | Total_BatDisEnergy | Uint32 | -2 | Kw h | R | Total battery discharge power
16599 | 40D7 | 2 | Today_InvGenEnergy | Uint32 | -2 | Kw h | R | Daily inverse electricity | Inverter power
16601 | 40D9 | 2 | Month_InvGenEnergy | Uint32 | -2 | Kw h | R | Monthly inverse electricity
16603 | 40DB | 2 | Year_InvGenEnergy | Uint32 | -2 | kw h | R | Annual inverse electricity
16605 | 40DD | 2 | Total_InvGenEnergy | Uint32 | -2 | Kw h | R | Total inverse power
16607 | 40DF | 2 | Today_TotalLoadEnergy | Uint32 | -2 | Kw h | R | Total daily load power consumption | The system load consumes power
16609 | 40E1 | 2 | Month_TotalLoadEnergy | Uint32 | -2 | Kw h | R | Total monthly load power consumption
16611 | 40E3 | 2 | Year_TotalLoadEnergy | Uint32 | -2 | Kw h | R | Annual total load power consumption
16613 | 40E5 | 2 | Total_TotalLoadEnergy | Uint32 | -2 | Kw h | R | Total load consumes power
16615 | 40E7 | 2 | Today_BackupLoadEnergy | Uint32 | -2 | Kw h | R | BackUp daily load consumes power | Backup load consumes power
16617 | 40E9 | 2 | Month_BackupLoadEnergy | Uint32 | -2 | Kw h | R | BackUp monthly load consumes power
16619 | 40EB | 2 | Year_BackupLoadEnergy | Uint32 | -2 | Kw h | R | BackUp annual load consumes power
16621 | 40ED | 2 | Total_BackupLoadEnergy | Uint32 | -2 | Kw h | R | BackUp total load consumes power
16623 | 40EF | 2 | Today_SellEnergy | Uint32 | -2 | kw h | R | Daily system sells electricity | R phase grid sells electricity
16625 | 40F1 | 2 | Month_SellEnergy | Uint32 | -2 | Kw h | R | Monthly system sells electricity
16627 | 40F3 | 2 | Year_SellEnergy | Uint32 | -2 | Kw h | R | Annual system sells electricity
16629 | 40F5 | 2 | Total_SellEnergy | Uint32 | -2 | Kw h | R | Total system sells electricity
16631 | 40F7 | 2 | Today_FeedInEnergy | Uint32 | -2 | Kw h | R | Daily system buys electricity | R phase grid buys electricity
16633 | 40F9 | 2 | Month_FeedInEnergy | Uint32 | -2 | Kw h | R | Monthly system buys electricity
16635 | 40FB | 2 | Year_FeedInEnergy | Uint32 | -2 | Kw h | R | Annual system buys electricity
16637 | 40FD | 2 | Total_FeedInEnergy | Uint32 | -2 | Kw h | R | Total system buys electricity
16695 | 4137 | 2 | Today_PV_Energy2 | Uint32 | -2 | Kw h | R | Daily PV2 Power generation | PV2 power generation
16697 | 4139 | 2 | Month_PV_Energy2 | Uint32 | -2 | Kw h | R | Monthly PV2 Power generation
16699 | 413B | 2 | Year_PV_Energy2 | Uint32 | -2 | Kw h | R | Annual PV2 Power generation
16701 | 413D | 2 | Total_PV_Energy2 | Uint32 | -2 | Kw h | R | Total PV2 Power generation
16703 | 413F | 2 | Today_PV_Energy3 | Uint32 | -2 | Kw h | R | Daily PV3 Power generation | PV3 power generation
16705 | 4141 | 2 | Month_PV_Energy3 | Uint32 | -2 | Kw h | R | Monthly PV3 Power generation
16707 | 4143 | 2 | Year_PV_Energy3 | Uint32 | -2 | Kw h | R | Annual PV3 Power generation
16709 | 4145 | 2 | Total_PV_Energy3 | Uint32 | -2 | Kw h | R | Total PV3 Power generation
16711 | 4147 | 2 | Today_SellEnergy2 | Uint32 | -2 | kw h | R | Daily amount of Grid2 electricity sold | S phase grid sells electricity
16713 | 4149 | 2 | Month_SellEnergy2 | Uint32 | -2 | Kw h | R | Monthly amount of Grid2 electricity sold
16715 | 414B | 2 | Year_SellEnergy2 | Uint32 | -2 | Kw h | R | Annual amount of Grid2 electricity sold
16717 | 414D | 2 | Total_SellEnergy2 | Uint32 | -2 | Kw h | R | Total amount of Grid2 electricity sold
16719 | 414F | 2 | Today_SellEnergy3 | Uint32 | -2 | kw h | R | Daily amount of Grid3 electricity sold | T phase grid sells electricity
16721 | 4151 | 2 | Month_SellEnergy3 | Uint32 | -2 | Kw h | R | Monthly amount of Grid3 electricity sold
16723 | 4153 | 2 | Year_SellEnergy3 | Uint32 | -2 | Kw h | R | Annual amount of Grid3 electricity sold
16725 | 4155 | 2 | Total_SellEnergy3 | Uint32 | -2 | Kw h | R | Total amount of Grid3 electricity sold
16727 | 4157 | 2 | Today_FeedInEnergy2 | Uint32 | -2 | Kw h | R | Daily amount of Grid2 electricity bought | S phase grid buys electricity
16729 | 4159 | 2 | Month_FeedInEnergy2 | Uint32 | -2 | Kw h | R | Monthly amount of Grid2 electricity bought
16731 | 415B | 2 | Year_FeedInEnergy2 | Uint32 | -2 | Kw h | R | Annual amount of Grid2 electricity bought
16733 | 415D | 2 | Total_FeedInEnergy2 | Uint32 | -2 | Kw h | R | Total amount of Grid2 electricity bought
16735 | 415F | 2 | Today_FeedInEnergy3 | Uint32 | -2 | Kw h | R | Daily amount of Grid3 electricity bought | T phase grid buys electricity
16737 | 4161 | 2 | Month_FeedInEnergy3 | Uint32 | -2 | Kw h | R | Monthly amount of Grid3 electricity bought
16739 | 4163 | 2 | Year_FeedInEnergy3 | Uint32 | -2 | Kw h | R | Annual amount of Grid3 electricity
16741 | 4165 | 2 | Total_FeedInEnergy3 | Uint32 | -2 | Kw h | R | Total amount of Grid3 electricity bought
16743 | 4167 | 2 | Sum FeedIn Today | Uint32 | -2 | Kw h | R | Sum of all phases Note: These register are not listed in the official PDF document of SAJ.
16745 | 4169 | 2 | Sum FeedIn Month | Uint32 | -2 | Kw h | R
16747 | 416b | 2 | Sum FeedIn Year | Uint32 | -2 | Kw h | R
16749 | 416d | 2 | Sum FeedIn Total | Uint32 | -2 | Kw h | R
16751 | 416f | 2 | Sum Sell Today | Uint32 | -2 | Kw h | R
16753 | 4171 | 2 | Sum Sell Month | Uint32 | -2 | Kw h | R
16755 | 4173 | 2 | Sum Sell Year | Uint32 | -2 | Kw h | R
16757 | 4175 | 2 | Sum Sell Total | Uint32 | -2 | Kw h | R